VEDLEGG 01 – ARBEIDSBESKRIVELSE 132 kV GIS Øygarden

APPENDIX 01 – WORK scope 132 kV GIS Øygarden

- INTRODUCTION

The project comprises the delivery and installation of a 145 kV Gas Insulated Switchgear (GIS) with environmentally friendly technology. The GIS contract will be novated into an EPC contract, and the interfaces to adjacent deliveries will be managed by a third party/contractor.

The switchgear will be under shared ownership between BKK and Statnett. BKK will act as the Purchaser and serve as the single point of contact within the scope of this contract.

- TECHNICAL REQUREMENTS

The technical requirements for the switchgear are specified in the Statnett SDOK system and are included in Vedlegg 07–22. Due to the shared ownership structure, the following two separate Special Specifications apply:

Vedlegg 07 – BKK Special specification

Vedlegg 08 – Statnett Special specification)

It should be noted that the principles for local control systems differ between BKK bays and Statnett bays.

The EPC contractor (on behalf of BKK) will be responsible for the construction of the substation building. Consequently, certain appendices referenced in the General Specifications are not applicable, including Appendix J – Specification for Substation Building.

The Special Specification for measuring transformers (SDOK-41-17) does not apply, as the technical requirements for these components are defined in Vedlegg 07 and Vedlegg 08.

The number of bays is specified in Vedlegg 22 – Single Line Diagram.

The equipment configuration, technical requirements, and rated values for the various parts of the switchgear are detailed in Vedlegg 07–22.

- MAINTENANCE

The GIS installation and gas compartmentalization shall be designed to facilitate future inspection and maintenance of all circuit breakers, allowing such work to be carried out while adjacent bays remain in operation.

The equipment shall comply with applicable IEC standards. A list of applicable standards shall be provided by the Supplier in the tender, refer to Vedlegg 10.

The Supplier shall provide descriptions of different scenarios for fault rectification, inspections, and maintenance of all circuit breakers. These scenarios shall clearly identify which parts of the installation must be de-energized in each case.

The maintenance programme, including associated costs, shall be provided to the Customer.