Long-term preventive service agreement for the two steam turbines at BIR Waste incineration plant in Rådal.

Technical Description

|  | Prepared by | Verified by | Approved by |
| --- | --- | --- | --- |
| Released for consultation | JOH | THB |  |
| Released for publication |  |  |  |
| Released for contract |  |  |  |

Table of Content

1	Scope of work	4

2	Description of scope	5

2.1	Inspection:	5

2.2	Minor overhaul	6

2.3	Major overhaul	6

2.4	Repair works	7

2.5	Helpdesk, Remote Support and Rapid Deployment of Personnel	7

2.6	Remote Access and Cyber Security Requirements	8

2.6.1	Remote Access and Authentication	8

2.6.2	Access Rights and Control System Responsibilities	8

2.6.3	Logging and Audit Trail	8

2.7	Special tools	9

2.8	Spare parts	9

2.9	Activity check list	9

2.10	Reports	9

2.11	Supplies, utilities and services	10

2.12	Customer responsibilities	10

2.13	Technical data	10

2.14	Operation	10

3	Plant description	11

3.1	General	11

3.2	Storage areas:	11

4	Operational description	12

4.1	Line 1	12

4.2	Line 2	12

5	Maintenance scheduling:	12

6	Line 1	13

6.1	Basic technical data of contract equipment	13

6.1.1	Steam turbine	13

6.1.2	Gear	13

6.1.3	Generator	14

6.1.4	Oil systems	14

6.2	Turbine hall layout and space	15

6.2.1	Turbine hall Line 1	15

6.3	List of drawings	17

6.4	Service reports	18

7	Line 2	19

7.1	Basic technical data of contract equipment	19

7.1.1	Steam turbine	19

7.1.2	Gear	19

7.1.3	Generator	20

7.1.4	Oil systems	20

7.2	Turbine hall layout and space	22

7.3	List of drawings	23

7.4	Service reports	24

# Scope of work

The scope of work under this Agreement is the provision of long-term preventive maintenance, technical support and supervision services for the two steam turbine-generator units and associated auxiliary systems at the BIR waste incineration plant in Bergen, Norway.

The scope shall include all necessary services and assistance required for the planning and execution of preventive and corrective maintenance of the two steam turbine-generator units, including but not limited to:

- Inspections

- Minor and major overhauls

- Remote service and telephone hotline

- Emergency service with short reaction time

- Spare parts supply

- Documentation

- Engineering support

When planning the maintenance programme, the service history and operating conditions of each turbine-generator unit shall be taken into account, including:

- Maintenance history

- Existing maintenance plans

- Existing maintenance records and protocols

- Standard maintenance procedures

- Relevant operational experience and condition monitoring data

Based on the available information, the Supplier shall establish and maintain a long-term maintenance plan, including the scope, timing and estimated duration of the various maintenance activities.

Definition of Customer

For the purpose of this Agreement, the term Customer shall mean:

- BIR Ressurs AS with respect to all services, equipment and activities related to the Line 2 steam turbine-generator unit.

- Eviny Varme AS with respect to all services, equipment and activities related to the Line 1 steam turbine-generator unit.

Unless otherwise specified, references to the Customer in this Agreement shall apply to the relevant party depending on the turbine-generator unit concerned.

# Description of scope

All works should be undertaken in accordance with the recommendations of the Original Equipment Manufacturer (OEM) as outlined in the attached standards or equivalent. See Figure 1.

Figure 1: OEM maintenance descriptions for ABB (line 1) and TGM Kanis (line 2) steam turbines at BIR.

This Technical Specification forms part of a maintenance contract based on Orgalime M 17. In case of conflict between this Technical Specification and other contract documents, the order of precedence shall be stated in the Contract.

Normal maintenance includes inspections, minor overhauls, major overhauls, testing, adjustment, reporting and replacement of agreed wear parts.

Repair work beyond normal maintenance is defined as repair not explicitly included in the preventive maintenance scope.

Repair is defined as work not explicitly included in the preventive maintenance scope

## Inspection:

Inspections between overhauls (minor and major), aims to maximize operational hours between overhauls. An inspection does not require the steam turbine to be opened. Auxiliary equipment/systems, may however, be dismantled to verify functionality as required.

Typical matters:

- Control system/control loops

- Technical questions

- Visual checks

- Oil quality/oil level

- Steam and condensate system/condensate traps

- Quick close device

- Trends

- Emergency oil pumps

- Over speed system

- Emergency stop switches

- Check of BIR inhouse special tools for the oncoming minor and major overhaul

- Inspection shall consider necessary spare parts and actions for oncoming minor or major overhaul. The existing spare parts shall be checked in respect for obsolescence.

## Minor overhaul

Minor overhaul does not require opening of the steam turbine casing. The minor overhaul shall as a minimum consist of OEM recommendations.

An overall overhaul plan, included in scope, shall be the guide to planning the schedule for minor overhauls. The intermediate inspections and follow up during operation shall be used to determine if the planned minor overhaul must take place before the overall schedule determines or be extended.

Follow up spare parts recommendations form intermediate inspection.

The work can comprise of:

- Operational questions

- Visual check of equipment

- Check of equipment

- Recommendation of adequate actions beyond normal maintenance (fact finding)

- Normal maintenance of equipment

- Re-mounting/installation of equipment

- Start-up, testing and adjustment of safety, control and supervision systems

- Documentation (Field service report)

- Recommendations for operation until next inspection/maintenance.

The maintenance shall also include the following options if agreed:

- Any additional repairs on site beyond the normal maintenance work discovered during fact finding.

The minor overhaul plan shall also have a backup plan if unplanned transport is deemed necessary for additional repairs.

## Major overhaul

The major overhaul shall as a minimum consist of OEM recommendations for a main overhaul. The supplier shall evaluate necessary actions beyond this to satisfy the purpose of this contract. The intermediate inspections and follow up during operation shall be used to determine if the planned minor overhaul must take place before the overall schedule determines or be extended.

Follow up spare parts recommendations form Intermediate inspection.

The work can comprise of:

- Preparation for opening of steam turbine

- Opening of steam turbine and removal of equipment

- Condition assessment and material testing

- Recommendation of adequate actions beyond normal maintenance (fact finding)

- Normal maintenance of equipment

- Re-mounting/installation of equipment

- Start-up, testing and adjustment of safety, control and supervision systems

- Documentation (field service report)

- Recommendations for operation until next inspection/maintenance.

The maintenance shall also include the following options if agreed:

- Any additional repairs on site beyond the normal maintenance work discovered during fact finding.

The major overhaul plan shall have a backup plan if unplanned transport is deemed necessary for additional repairs.

## Repair works

If inspections, minor overhauls or major overhauls reveal defects requiring repair work beyond normal maintenance, the Supplier shall prepare a written repair proposal.

No repair work beyond the agreed maintenance scope shall commence before written approval from the Customer.

Unless otherwise agreed, the repair work shall be handled as corrective maintenance under M 17. If ordered as a separate repair assignment outside the maintenance contract, Orgalime R 17 may apply.

## Helpdesk, Remote Support and Rapid Deployment of Personnel

The remote service shall include:

- 24-hour telephone hotline service

- Troubleshooting by telephone

- Troubleshooting, fault diagnostics and condition monitoring through remote access to the Customer's SCADA and control systems, including analysis of trend data, alarm logs, event logs and historical operating data. Any remote access required for such activities shall be granted in accordance with Section 2.6 Remote Access and Cyber Security Requirements.

- Rapid deployment of service personnel within 72 hours of the Customer's request for assistance. Adequately qualified service personnel, as agreed with the Customer, shall be mobilized and present on site within this timeframe.

- Continuous review and update of the maintenance programme, including planning of major and minor overhauls.

## Remote Access and Cyber Security Requirements

The Supplier shall not establish, install or activate any remote access solution without BIR's prior written approval. BIR reserves the right to suspend or revoke remote access privileges at any time for operational, safety or cyber security reasons.

### Remote Access and Authentication

- All remote access shall be routed exclusively through BIR's VPN. Supplier-managed cloud relays, gateways or remote access services are not permitted.

- Authentication shall be performed through BIR's SAML-based Single Sign-On (SSO) solution with Multi-Factor Authentication (MFA) enabled.

- BIR shall maintain an approved persons access list. Only named individuals approved by BIR shall be granted access.

- The Supplier shall ensure that the approved persons list remains accurate and up to date and shall notify BIR without undue delay of any personnel changes, including onboarding and offboarding.

### Access Rights and Control System Responsibilities

- Remote access shall be limited to read-only access unless otherwise approved in writing by BIR.

- No write access, software modifications, parameter changes, configuration changes or control logic changes are permitted without prior written authorization from BIR.

- Any modification of turbine automation, software, code or control logic shall only be performed by:

  - Line 1 turbine system: Valmet or personnel approved by Valmet.

  - Line 2 turbine system: TGM Kanis.

- Any approved modification shall be documented and reported to BIR after completion.

### Logging and Audit Trail

- All remote access sessions will be logged, including user identity, access times, duration and activities performed.

- Access logs will be retained in accordance with NIS2 and IEC 62443 requirements.

## Special tools

The supplier is responsible for necessary special tools.

## Spare parts

The supplier shall recommend spare parts stock and planning with unit prices. The spares may be located at BIR or locally at supplier. The recommendation shall define capital spares and long lead items. Spare parts withdrawn from storage during maintenance shall be replaced as soon as possible. The spare parts shall be solely owned by Customer.

To achieve simple import of data to BIR maintenance system the spare parts should be listen in an Excel file. The Supplier shall clarify the required file format with BIR before preparing and submitting the documentation.

## Activity check list

There shall be a suggestion of activity and task check list for the scope of supply. The list shall define who has the responsibility for the different tasks and activities.  The list shall define necessary assistance from Customer personnel.

## Reports

There shall be a concluding report after each service and maintenance visit. The report shall minimum include:

- Description of conducted maintenance and work.

- Pictures for illustration, specifically for identifying necessary maintenance actions.

- Conclusions and recommendations for further work and maintenance

- Reports shall be in Norwegian

- Shall be in electronic format

## Supplies, utilities and services

The following utilities are accessible in the turbine buildings:

- Compressed air

- Electricity, 440V, 240 V

- Water

- Fire extinguisher

- Necessary scaffolding (planned use of scaffolding must be defined by supplier in advance to site visits)

Personal safety equipment to be held by the supplier:

- The personnel shall use safety equipment according to the regulations at BiR.

- All staff must undertake required site induction before performing any activities.

## Customer responsibilities

The Customer shall, upon request from the Supplier and within agreed time before the outage:

- Remove insulation as required to provide access to equipment under maintenance.

- Remove and reinstall sprinkler systems where necessary to enable maintenance activities.

- Provide and arrange required scaffolding.

- Ensure generator earthing and all required electrical isolations according to site safety procedures.

The Supplier shall inform the Customer in sufficient time before the outage regarding the scope and extent of these requirements.

## Technical data

All technical data Customer has received from the OEM will be available. In the case of additional information being required, it is expected that the supplier contact the OEM.

## Operation

The Customer shall operate and monitor the Equipment in accordance with good industry practice. Operational records, event logs and performance data shall be made available to the Supplier upon request.

# Plant description

## General

The turbines are physically located in the BIR waste incineration facility located in Rådal.  The steam supply to the turbines is supplied by boilers in the incineration facility.  Steam from the boilers can also be delivered via pressure reduction valves, directly to the district heating plant in the neighbouring building or be dumped directly to the condensers.

The plant is constructed in 2 separate and independent lines, each with it’s own waste heat boiler, steam turbine and power generator.

Line 1

The turbine on Line 1 is a condensing turbine, and steam is extracted from the turbine to supply the district heating plant in the neighbouring building, and exhaust steam from the turbine goes to air cooled condensers.

Both the turbine on Line 1 and the neighbouring district heating plant is owned by Eviny, and operated by BIR Avfallsenergi.  The equipment is controlled and monitored from the control room at the incineration facility.

Line 2

The turbine on Line 2 can operate in either condensing or back pressure mode.  Exhaust steam from the turbine delivers heat to district heating plant via heat exchanges located in the BIR facility; or to the air-cooled condensers.

## Storage areas:

Appropriate areas for storage of equipment during maintenance works will be made accessible to the supplier as required.

# Operational description

The operation of the turbosets on line 1 and 2 differ; the operation is summarised briefly in this section.  The facility aims to cover 100% of the district heating demand, with remaining heat utilised in electricity production.

## Line 1

The turbine on Line 1 is typically operational if Line 1 is running.  However, in periods of high district heating demand, the turbine on Line 1 operates in turning gear; with steam being supplied to the district heating plant in the neighbouring building.

The expected annual operating time of the Line 1 turbine is approximately 5500 hours.

## Line 2

The turbine on line 2 operates in conjunction with district heating delivery. The turbine, therefore, is operational throughout the year if Line 2 is running.

The expected annual operating time of the Line 2 turbine is approximately 8000 hours.

# Maintenance scheduling:

Maintenance and service on the steam turbines should be conducted to cause least possible operational disturbance and economic loss.  It is therefore important that all work on the turbines should be planned to ensure shortest possible downtime.

When the steam turbines are out for service and maintenance, the steam is in bypass to the heat exchangers for municipal heat.

When planning services, the following conditions should be considered:

- The incineration process and associated boiler will be operational.

- Steam systems and steam delivery to the district heating plant will be operational.

- The systems for dumping steam to the air cooler shall be fully available.

# Line 1

Information regarding Line 1 is outlined in this section.

## Basic technical data of contract equipment

The basic technical data for the equipment is described in this chapter. The following equipment shall be included in the scope:

- Steam turbine

- Gear

- Generator

- Oil system (lube and control)

- Seal and gland steam system

- Local instrumentation on equipment

- Safety functions including associated instrumentation

- Emergency steam turbine drives

### Steam turbine

| Turbine |  |
| --- | --- |
| Make | ABB Turbinen Nürnberg GmbH |
| Type | ATP2 - VE 40A |
| Serial number | 19333 |
| Year | 1999 |
| Rpm | 7554 |
| Rated power | 10 800 kW |
| Stages | 5+9 |
| Steam conditions in | 38 bara / 395oC |
| Steam flow | 15.1 kg/s |
| Steam conditions out | 0.085-0.115 bara / 45oC |
| Control valves | 3 |
| Nozzle groups | 3 groups – in the under nozzle chamber, welded to the under turbine casing section |
| Control wheel | Impulse blading single wheel |
| Guide blade carriers | 3 sets |

### Gear

| Gear |  |
| --- | --- |
| Make | Flender Graffenstaden |
| Type | X 63/5 |
| Year | 1999 |
| Rpm: XXX/YYY | 7554 / 1500 |

### Generator

| Generator |  |
| --- | --- |
| Make | ABB |
| Type | AMS 900 SG |
| Year | 1999 |
| Nominal power | 13 500 kW |
| Voltage | 11 kV |
| Current | 709 A |
| Rpm | 1500 |
| Weight rotor | 3 258 kg |

### Oil systems

| Lube Oil Tank |  |
| --- | --- |
| Contents | 10 000 L |
| Capacity | Approx. 10 700 L |
| Number of circuits | 7.5 h-1 |
| Retention time | 8 min |
| Manufacturer | Hoffmann |
| Suction capacity | 45 m3/min |
| Slight Vacuum | 20 mbar |
| Output motor | 0.77 kW |
| Voltage | 400 V |
| Frequency | 50 Hz |

| Oil-Plant General Data |  |
| --- | --- |
| Oil quality | ISO VG 46 |
| Control oil pressure | 8 barg |
| Lube oil pressure | 2 barg |
| Bearing oil pressure | 1.2 barg |
| Lube oil temperature | 49oC |
| Oil pumps |  |
| Main oil pump make | Allweiler |
| Main oil pump size | 1 250 L/min / 22 kW |
| Auxiliary oil pump make | Allweiler |
| Auxiliary oil pump size | 12 50 L/min / 22 kW |
| Emergency oil pump make | Allweiler |
| Emergency oil pump size | 348 L/min / 2.2 kW |

## Turbine hall layout and space

The access to the turbine halls is by use of doors in the wall and by openings in the floor. Overhead cranes are dimensioned according to necessary lifting capacity.

### Turbine hall Line 1

Floor area:					23 × 12.5 m

Ceiling height:					4.5 m

Exterior entrance:				3.8 × 3.8 m

Entry from incineration facility:		standard doors

Lifting capacity overhead crane: 	10 tonne

Figure 2 Line 1 turbine

Turbine house:

Dimensions:					13×6.5×4.5 m (LxBxH)

The top of the casing is easily removable and can be moved with the overhead crane located in the turbine hall.  It is possible to lift turbine and gear parts out without removing the walls of the casing.

Figure 3  Line 1 turbine housing

## List of drawings

Drawing list for information:

| Name | Drawing reference | Date |
| --- | --- | --- |
| Sectional drawing | K19333-000 | 02/09/08 |
| P&ID closed cooling water system | 0000 5498 | 07/10/97 |
| P&ID feed water pipes | 0000 5495 | 07/10/97 |
| P&ID HP steam pipes | 0000 5482 | 16/09/97 |
| P&ID boiler blow down pipes | 0000 5497 | 19/01/98 |
| P&ID piping drain | 0000 5492 | 19/01/98 |
| P&ID condensate pipes deionized water pipes | 0000 5505 | 07/10/97 |
| P&ID 2.7 bar steam pipes | 0000 5491 | 19/02/98 |
| P&ID IP de-superheating spray system | 0000 5496 | 23/03/98 |
| P&ID 8 bar steam pipes | 0000 5490 | 23/09/97 |
| General arrangement look down | 1CWK027487 | 12/11/99 |
| Steam system | 1CWK027497 | 09/10/98 |
| Drain system | 1CWK027498 | 09/06/98 |
| Sealing system | 1CWK027499 | 16/07/98 |
| Oil supply system | 1CWK027500 | 11/08/98 |
| Oil consumer system | 1CWK027501 | 13/10/98 |
| Cooling system | 1CWK027502 | 24/08/98 |
| Vibration measurement | 1CWK027503 | 09/09/98 |

Access to drawings will be granted upon request, subject to the Supplier having signed and returned the NDA. Please refer to Section 1.4 of the Tender Conditions.

## Service reports

Service reports for information:

| Name | Date |
| --- | --- |
| Condition Assessment / No-Stop Inspection | January 2018 |
| NDT Inspection during Minor Overhaul | September 2021 |
| Minor Overhaul Completion Report | February 2022 |
| Generator Condition Assessment (L3 Inspection) | March 2022 |
| Turbine Protection & Monitoring System Upgrade | December 2023 |
| Bearing NDT Inspection | December 2024 |
| Split Line Condition Assessment and Repair Recommendation | December 2024 |
| Repair Scope Definition for Major Overhaul | January 2025 |
| Fact Finding Inspection for Major Overhaul | January 2025 |
| Major Overhaul Completion Report | June 2025 |

Access to Service reports will be granted upon request, subject to the Supplier having signed and returned the NDA. Please refer to Section 1.4 of the Tender Conditions.

# Line 2

Information regarding Line 2 is outlined in this section.

## Basic technical data of contract equipment

The basic technical data for the equipment is described in this chapter. The following equipment shall be included in the scope:

- Steam turbine

- Gear

- Generator

- Oil system (lube and control)

- Seal and gland steam system

- Local instrumentation on equipment

- Safety functions including associated instrumentation

- Emergency steam turbine drives

### Steam turbine

| Turbine |  |
| --- | --- |
| Make | TGM Turinas |
| Type | BT32 |
| Rpm | 8 500 |
| Rated power | 9 600 kW |
| Stages | 15 |
| Steam conditions in | 41 bara / 400oC |
| Steam flow | 59.8 t/h (max) |
| Bleed 1 | 6.4 bara / 191oC |
| Bleed 2 | 3.4 bara / 186oC |
| Bleed 3 | 3.4 bara / 186oC |
| Exhaust | 0.6-2.4 bara / 94-210oC |

### Gear

| Gear |  |
| --- | --- |
| Make | Renk |
| Type | TCS-630 |
| Model | Double-helical spur wheel gearbox |
| Nominal power | 10 020 kW |
| Transmission ratio | 5.63 : 1 |
| Turning gear | Over sss-coupling on free shaft end of the gearbox |
| Make / Type | Renk / TV 03 |
| Drive | Electric motor |
| Power | 15 kW |
| Voltage / frequency | 400 V / 50 Hz |
| Motor speed | 2 930 min-1 |
| Rotation speed rotor turning drive | 353 min-1 |

### Generator

| Generator |  |
| --- | --- |
| Make | Converteam |
| Type | A132X4 |
| Rating | 8 327.2 kW |
| Rating | 10 409 kVA |
| Voltage | 11 kV |
| cos fi | 0.8 |
| Frequency | 50 Hz |
| Rpm | 1500 min-1 |

### Oil systems

| Lube oil tank |  |
| --- | --- |
| Manuafacturer | Buhlmann-Project-Solutions |
| Dimensions (L×B×H) | 3 488 × 3 585 × 571mm |
| Oil volume | 5 000 L |
| Residency time | 8 min |
| Recirculations | < 7.5 h-1 |

| Oil-plant general information |  |
| --- | --- |
| Oil quality | ISO VG 46 |
| Control oil pressure | 8 barg |
| Lube oil pressure | 2 barg |
| Position of oil coolers | Vertical |
| Cooling water inlet temperature | 30oC |
| Differential pressure cooling water | 0.61 barg |
| Cooling water quality | Water-glycol mixture |
| Cooling water rate | ~ 7.916 kg/s |
| Oil pumps |  |
| Main oil pump make | Allweiler |
| Main oil pump capacity | 747 L/min |
| Auxiliary oil pump make | Kral |
| Auxiliary oil pump capacity | 667.4 L/min / 16.43kW |
| Emergency oil pump make | Kral |
| Emergency oil pump capacity | 225.9 L/min / 2.44kW |

## Turbine hall layout and space

The access to the turbine halls is by use of doors in the wall and by openings in the floor. Overhead cranes are dimensioned according to necessary lifting capacity.

Exterior entrance:				4 × 6.5 m through service hatch

Entry from incineration facility:		standard doors

Lifting capacity overhead crane: 	10 tonne

Figure 4 Line 2 turbine

Figure 5  Line 2 turbine service hatch

## List of drawings

Drawing list for information:

| Name | Drawing reference | Date |
| --- | --- | --- |
| Turbine casing alignment scheme | 1.01.2590.00.2 | 12/02/09 |
| Turbine steam system | 90006725 | 16/04/10 |
| Turbine drainage | 90006726 | 16/04/10 |
| Sealing leaking steam | 90006727 | 16/04/10 |
| Oil feed | 90006728 | 16/04/10 |
| Oil consumer | 90006729 | 16/04/10 |
| Vibration measuring | 90006730 | 16/04/10 |
| Cooling system turbine | 90006731 | 16/04/10 |
| Water treatment plan | 90006732 | 16/04/10 |
| Water steam system | 90006824 | 19/08/09 |

Access to drawings will be granted upon request, subject to the Supplier having signed and returned the NDA. Please refer to Section 1.4 of the Tender Conditions.

## Service reports

Service reports for information:

| Date | Report name / activity |
| --- | --- |
| September 2019 | BIR Bergen Line 2 Turbine and Generator D2 Level Inspection 2019. D2-level inspection of the turbine, gearbox and generator, including turbine endoscope inspection. |
| October 2019 | TGS-01532 BIR/BKK Line 2; Inspection. Visual inspection of the generator and associated components. |
| October 2020 | BIR Bergen Line 2 Turbine and Generator Minor Overhaul NDT and Endoscope Inspection 2020. NDT and endoscope inspection during the minor overhaul. |
| 2020 | Measurement Protocol, BIR Avfallsenergi AS, TGM Kanis Turbine Minor Overhaul, Line 2, 2020. Measurement of turbine, gearbox and generator bearing clearances and axial positions. |
| October 2020 | TGS-02527 Diagnostic Test Records / Generator Electrical Measurements. Electrical diagnostic measurements of the generator, rotor and excitation system. |
| November 2020 | BIR Avfallsenergi AS, TGM Kanis Turbine Minor Overhaul, Line 2, 2020. Minor overhaul of turbine, bearings, valves, actuators and gearbox. |
| December 2020 | BIR Bergen Line 2 Commissioning After Start Up Problems. Troubleshooting and commissioning following generator overvoltage and vibration trips. |
| January 2021 | Equipment Test Report, Stator Winding. ABB electrical testing of the generator stator winding. |
| September 2021 | BIR Bergen Line 2 Turbine and Generator Endoscope Inspection 2021. Endoscope inspection of the turbine and generator and visual inspection of the gearbox. |
| December 2022 | TGM Kanis Steam Turbine and Renk TCS-630 Gearbox Major Overhaul 2022. Major overhaul of the steam turbine and gearbox. |
| March 2023 | TGS-03732 Bergen BIR Line 2 MO Generator 2022. Major overhaul and condition assessment of the Line 2 generator. |
| March 2023 | TGS-03732 Appendices, Basis for Diagnostic and Diagnostic Test Records. Detailed inspection records, measurements, NDT reports and deviation records from the generator major overhaul. |
| July 2023 | TGS-04299 Rotor Earth Fault System Diagnostics. Troubleshooting and corrective work following repeated rotor earth-fault trips. |
| April 2024 | TGS-05072 Island Mode Test, Phase 1. Testing of breaker signals, turbine control, bypass operation and excitation during transition to island mode. |
| July 2024 | TGS-05072 Island Mode Test, Phase 2. Testing of turbine speed control, bypass operation, generator voltage control and island-mode signal stability. |
| October 2025 | TGS-06496 Valve Test, Bergen Line 2 BIR 2025. Stroke, response, partial-stroke and quick-closing tests of the control valves and emergency stop valve. |
| October 2025 | TGS-06509 Turbine Endoscope and Gearbox Inspection 2025. Endoscope inspection of the turbine and visual inspection of the gearbox and associated components. |
| January 2026 | TGS-06907 Generator Electrical Connection Inspection 2025. Inspection of electrical connections, phase sequence and synchronising circuits following the generator-transformer failure. |
| February 2026 | TGS-06857 Generator Measurements After Transformer Fault 12-2025. Electrical and visual condition assessment of the generator following the generator-transformer failure. |

Access to Service reports will be granted upon request, subject to the Supplier having signed and returned the NDA. Please refer to Section 1.4 of the Tender Conditions.